## R32 DN Codes_WM
Location & DN Number
| DN Description | Hydro | RC | Range HWT-60 (HWT-110) | Default HWT-60 (HWT-110) | After Commissioning | Change 1 | Change 2
Setting Water Temperature Range | Heating Upper Limit - Zone 1 | 1A | - | 37~55°C (65°C) | 55 (65)
| Heating Lower Limit - Zone 1 | 1B | - | 20~37°C | 20
| Heating Upper Limit - Zone 2 | 1C | - | 37~55°C (65°C) | 55 (65)
| Heating Lower Limit - Zone 2 | 1D | - | 20~37°C | 20
| Cooling - Upper Limit | 18 | - | 18~30°C | 25
| Cooling - Lower Limit | 19 | - | 7~20°C | 7
| Hot Water - Upper limit | 1E | - | 60~80 | 75
| Hot Water - Lower limit | 1F | - | 40~60°C | 40
Hot Water Operation | Heat Pump Start Temperature | 20 | - | 20~45°C | 38
| Heat Pump Stop Temperature | 21 | - | 40~65°C | 52
| Group control - connection of TTW sensor: 0 = TTW sensor to be connected to each hydro unit 1 = TTW value transmitted from the HEADER unit | AB | - | 0~1 | 0
| Hot water tank heater start time of heat-pump while operating 0 = 30min passed 1 = 60min passed 2 = 90min passed 3 = 120min passed | 73 | - | 0~3 | 3
Hot Water Temperature Compensation | Temperature Compensation Outside Air Temperature (°C) | 24 | - | -20~10°C | 0
| Compensation Temperature (°C) | 25 | - | 0~15°C | 3
Hot Water Boost | Operation Time (x10 min) | 08 | - | 3~18 | 6
| Setting Temperature (°C) | 09 | - | 40~80 | 75
Anti Bacteria | Setting Temperature (°C) | 0A | - | 60~80 | 75
| Start Cycle (Day) | - | 0D | 1~10 | 7
| Start Time (Hour) | - | 0C | 0~23 | 22
| Operation Time (min) | 0B | - | 0~60 | 30
Priority Mode | Hot Water & Heating Switching Temperature (°C) | 22 | - | -40~20°C | 0
| Boiler & Heat Pump Switching Temperature (°C) | 23 | - | -20~20°C | -10
| Hot Water & Cooling priority selection: 0 = Cooling priority. Hot water produced by electric heater 1 = Hot water priority. Hot water produced by HP | 0F | - | 0~1 | 0
Heating Auto Curve Settings | Outside air temperature T0 (°C) | A1 | - | -20 (-30) ~ -15 (-20)°C | -20
| Outside air temperature T1 (°C) | 29 | - | -15~0°C | -10
| Outside air temperature T3 (°C) | 2B | - | 0~15°C | 10
| Setting Temperature A @ T0 (°C) - Zone 1 | 2C | - | 20~55°C (65°C) | 40
| Setting Temperature B @ T1 (°C) - Zone 1 | 2D | - | 20~55°C (65°C) | 35
| Setting Temperature C @ T2 (°C) - Zone 1 | 2E | - | 20~55°C (65°C) | 30
| Setting Temperature D @ T3 (°C) - Zone 1 | 2F | - | 20~55°C (65°C) | 25
| Setting Temperature E @ OAT 20°C (°C) - Zone 1 | 30 | - | 20~55°C (65°C) | 20
| Ratio Of Zone 2 In Zone 1 Auto Mode (%) | 31 | - | 0~100% | 80
| Zone 2 temperature setting 0=% (DN_31) ; 1 = Fixed (DN_A3~A5) | A2 | - | 0~1 | 0
| Setting temperature A' at T0 (°C) - Zone 2 | A3 | - | 20~55°C (65°C) | 40
| Setting temperature B' at T1 (°C) - Zone 2 | A4 | - | 20~55°C (65°C) | 35
| Setting temperature E' at 20°C (°C) - Zone 2 | A5 | - | 20~55°C (65°C) | 20
| Auto Curve - Temperature Shift (°C) | 27 | - | -5~5°C | 0
Frost Protection | Function 0=Invalid; 1=Valid | 3A | - | 0~1 | 1
| Frost Protection Setting Temperature (°C) | 3B | - | 8~20°C | 15
| Schedule end day | - | 12 | 0~20 | 0
| Schedule end time | - | 13 | 0~23 | 0
Back Up Heater Control | Downtime Back Up Heater 0=5min; 1=10min; 2=15min;3=20min | 33 | - | 0~3 | 1
| Uptime Back Up Heater 0=10min; 1=20min; 2=30min; 3=40min | 34 | - | 0~3 | 0
| Back up heater FORCE OFF at T0≥A°C: 0=no restriction; 1=20°C, 2=15°C….......6=-5°C | B8 | - | 0~6 | 0
| Back up heater operation during defrost control: β = TSC_F - THO 0 = 0K; 1 = 10K, 2 = 20K, 3 = 30K; 4 = 40K Recommendation: β = 2 = 20K | B9 | - | 0~4 | 0
| Backup heater capacity 0 = 3kW 1 = 6kW 2 = 9kW | 6BC | - | 0~2 | Depend on type
Night Setback | Change Setback Temperature (°C) | 26 | - | 3~20°C | 5
| Zone selection 0=Zone 1 & 2; 1= Zone 1 Only | 58 | - | 0~1 | 0
| Start Time (Hour) | - | 0E | 0~23 | 22
| End Time (Hour) | - | 0F | 0~23 | 6
Room Temperature Remote Controller | Temperature sensor using in room temperature control 0 = OFF 1 = ON | - | 1E | 0~1 | 0
| Room temperature control: 0 = Invalid; 1 = valid | 40 | - | 0~1 | 0
| Setting room temperature range: Cooling room temperature upper limit | 92 | - | 0 ~ 55 | 29
| Setting room temperature range: Cooling room temperature lower limit | 93 | - | 0 ~ 55 | 18
| Setting room temperature range: Heating room temperature upper limit | 94 | - | 0 ~ 55 | 29
| Setting room temperature range: Heating room temperature lower limit | 95 | - | 0 ~ 55 | 18
| Initial target water temperature in cooling with either room temperature controller or external room thermostat | 96 | - | 5 ~ 30 | 20
| Initial target water temperature in heating with either room temperature controller or external room thermostat | 9D | - | 20~55 (65) | 40
| Sets HP start temperature (water) when control is in A zone (2nd RC option only) | B2 | - | 20 ~ 37 | 25
| Initial water temperature setting method when controlling heating by the room temperature remote controller and room temperature thermostat: 0=Fixed temperature (DN_9D); 1=Calculated by Auto Curve (first time power up ONLY) | B5 | - | 0~1 | 0
| Room temperature offset: Heating room temperature offset value (sensor temp - control temp, K) | - | 02 | -10~10 | -1
| Room temperature offset: Cooling room temperature offset value (sensor temp - control temp, K) | - | 03 | -10~10 | -1
Hydro 2 Way Valve Operation Control | Cooling 2 Way Valve - Operation Logic: 0=Activated during cooling; 1=Not activated during cooling | 3C | - | 0~1 | 0
| DN Description | Hydro | RC | Range HWT-60 (HWT-110) | Default HWT-60 (HWT-110) | After Commissioning | Change 1 | Change 2
Hydro 3 Way Diverting Valve Operation Control | 3 Way Diverting Valve Operation Logic: 0=Activated during hot water operation; 1=not activated during hot water operation | 54 | - | 0~1 | 0
2 Zone Mixing Valve Drive Time | Specified Drive Time for Mixing Valve (x10sec) | 0C | - | 3~24 | 6
| Mixing valve OFF (control time - mins) 0=30sec; 1~30min | 59 | - | 0 = 30 sec, 1~30min | 2
| Temperature difference for mixing valve opening value changing | 6F1 | - | 1~3 | 2
| Mixing valve maximum steps | 6F2 | - | 12~60 | 24
Boiler/Heat Pump Synchronisation | External Boiler/Heat Pump Synchronisation 0=Synchronised, external boiler stops as temperature reaches the hydro unit's temperature setting ; 1=Not synchronised | 3E | - | 0~1 | 0
| System Operation during low ambient conditions: 0 = HP + boiler operation 1 = Boiler only operation (Pump P1 RUN) 2 = Electric heater only operation 3 = Boiler only (Pump P1 STOP) | 5B | - | 0~3 | 3
| Enable / Disable error code A02 (high return water control): 0 = A02 enabled 1 = A02 disabled | 62 | - | 0~1 | 0
| Used to activate external boiler output: 0 = external boiler output de-activated 1 = external boiler output activated | 6B0 | - | 0~1 | 0
| Boiler install location: 0 = Heating side after 3 way diverting valve 1 = Before 3 way diverting valve | 6B1 | - | 0~1 | 0
Maximum Operation Time Of Hot Water Heat Pump | Maximum Heat Pump Operation Time In Hot Water Operation Priority Mode (minutes) | 07 | - | 1~120 | 30
Cooling Operation | Select cooling mode: 0=Cooling & Heating Operation; 1=Heating Only Operation | 02 | - | 0~1 | 0
Remote Controller Indication | 24h or 12h Time Indication 0= 24h; 1=12h | - | 05 | 0~1 | 0
CDU Night Time Low Noise Operation | Low Noise Operation 0=Invalid; 1=Valid | - | 09 | 0~1 | 0
| Start Time (Hour) | - | 0A | 0~23 | 22
| End Time (Hour) | - | 0B | 0~23 | 6
Alarm Tone | Tone Switching 0=OFF; 1=ON | - | 11 | 0~1 | 1
Pump Control | Pump P1 operation during DHW mode: 0 = synchronised with heat pump 1 = Normal / continuous operation | 5A | - | 0~1 | 0
| Pump P2 operation in cooling mode: 0 = P2 continuous operation 1 = P2 stops in cooling operation | 64 | - | 0~1 | 0
| Synchronises pump P1 with room temperature control: 0 = P1 runs continuously 1 = P1 synchronised with room temperature control. When using the room temperature controller or the external room thermostat P1 will stop when HP in thermo OFF mode | 65 | - | 0~1 | 0
| Pump P1 operation: OAT temperature control in heating mode: P1 stops when TO > set value in DN_9E and DN_6D0=1 (heating mode only) | 9E | - | 10~30 | 20
| TO diff temperature, when pump P1 stop at TO 20°C | 6E | - | 1~5 | 2
| A-rated pump (P1) speed control. Changes the percentage duty of the PWM control. 00 = 100% PWM duty (Max. RPM) 01 = 90% ; 02 = 80%; 03 = 70%; 04 = 60% 05 = 50% | A0 | - | 0~5 | 0
| Pump P1 speed control method: 0 = fixed speed control (using DN_A0) 1 = variable speed control | 6A6 | - | 0~1 | 1
| Pump P1 speed correction for variable speed pump control: 0=100% Flmax; 1=90% Flmax; 2=75% Flmax; 3=50% FLmax | 6A7 | - | 0~3 | 0
| Pump P2 synchronisation: 0 = P2 continuous operation (P2 OFF when RC OFF) 1 = Synchronised with pump P1 | 6B5 | - | 0~1 | 0
| Pump P1 operation with OAT control: 0 = Normal / continuous operation 1 = P1 stopped when TO > 20°C | 6D0 | - | 0~1 | 0
| Pump P1 ON/OFF cycling (during long periods of system OFF) 0 = Normal / continuous operation 1 = Intermittent operation Must be used with DN_BA (HTG.) and DN_BB (CLG.) | 6D1 | - | 0~1 | 0
| Pump P1 Intermittent operation when T0 ≥ A°C (HTG.) 0 = continuous operation; 1 = 20°C; 2 = 15°C; 3 = 10°C; 4 = 5°C; 5 = 0°C; 6 = -5°C | BA | - | 0~6 | 0
| Pump P1 Intermittent operation when T0 < B°C (CLG.) 0 = continuous operation; 1 = 35°C; 2 = 30°C; 3 = 25°C | BB | - | 0~3 | 0
| Pump P2 on wireless adaptor screen (not on RC display): 0=Not Shown; 1=Shown | 42 | - | 0~1 | 0
| Pump off time during thermostat off operation 0 = 5min 1 = 10min … 5 = 30min | BC | - | 0~5 | 1
| DN Description | Hydro | RC | Range HWT-60 (HWT-110) | Default HWT-60 (HWT-110) | After Commissioning | Change 1 | Change 2
Operation By External Digital Input (optional) | Input signal setting when using I/P7 / 8 (CN21) as an a forced system STOP (and DN_B6 = 0) 0 = Contacts low > high system stop. System restart with remote controller 1 = Contacts high > low system stop. System restart with remote controller | 52 | - | 0~1 | 0
| Input signal setting when using I/P5 / 6 (CN21): 0 = Contacts high > low system STOP. Contacts low > high system restart 1 = Contacts low > high system STOP. Contacts low > high (2nd time - pulse input) system restart | 61 | - | 0~1 | 0
| Custom options for I/P7 / 8 (CN21): 0: I/P 7 = Forced stop input; I/P 8 = None 1: I/P 7 = TEMPO 1 input; I/P 8 = None 2: I/P 7 = TEMPO 2 input; I/P 8 = None 3: I/P 7 = Forcibly turn OFF bach up heater; I/P 8 = Forcibly turn OFF the hot water tank heater 4: I/P 7 = SMART Grid network input 1; I/P 8 = SMART Grid network input 2 | B6 | - | 0~4 | 0
Hydro Unit Digital Outputs | Output 1 options: 0 = alarm output 1 = Compressor operation output 2 = Defrost operation output 3 = Boiler control output 4 = Safety or protection control running 5 = Back up heater ON 6 = DHW cylinder heater ON 7 = Heating mode ON 8 = Cooling mode ON 9 = DHW mode ON | 6CA | - | 0~9 | 0
| Output 2 options: 0 = alarm output 1 = Compressor operation output 2 = Defrost operation output 3 = Boiler control output 4 = Safety or protection control running 5 = Back up heater ON 6 = DHW cylinder heater ON 7 = Heating mode ON 8 = Cooling mode ON 9 = DHW mode ON | 6CC | - | 0~9 | 2
| Output 3 options: 0 = alarm output 1 = Compressor operation output 2 = Defrost operation output 3 = Boiler control output 4 = Safety or protection control running 5 = Back up heater ON 6 = DHW cylinder heater ON 7 = Heating mode ON 8 = Cooling mode ON 9 = DHW mode ON | 6CD | - | 0~9 | 3
| Output 4 options: 0 = alarm output 1 = Compressor operation output 2 = Defrost operation output 3 = Boiler control output 4 = Safety or protection control running 5 = Back up heater ON 6 = DHW cylinder heater ON 7 = Heating mode ON 8 = Cooling mode ON 9 = DHW mode ON | 6CB | - | 0~9 | 1
Hydro Unit Type Setting | Hydro unit type setting: 70 = wall mounted hydro unit 71 = All In One type hydro unit | 10 | - | 70 or 71 | Depends on Hydro Unit
Hydro Unit Capacity Setting | Water heat exchanger capacity: 0010 = 401 / 601 0015 = 801 / 1101 | 11 | - | 0010 or 0015 | Depends on Hydro Unit
Outdoor unit type setting | Outdoor unit type setting 0 = 401/601 1 = 801/1101 2, 3 = None | 6BD | - | 0~3 | Depend on type
Floor Drying | Floor drying setting 0 = OFF 1 = ON | - | 1D | 0~1 | 0
| Setting START and END temperature (°C) | - | 14 | 20~55 | 0
| Setting maximum temperature (°C) | - | 15 | 20~55 | 0
| Continuation days for every step up to maximum temperature (days) | - | 16 | 1~7 | 0
| Temperature difference for every step up to maximum temperature (K) | - | 17 | 1~10 | 0
| Continuation days for every step down to end temperature (days) | - | 18 | 1~7 | 0
| Temperature difference for every step down to end temperature (K) | - | 19 | 1~10 | 0
| Continuation days at maximum temperature (days) | - | 1A | 1~50 | 0
0-10V Interface (optional) | ESTIA control type: 0 = Normal control 1 = Setpoint temperature control (DN_681~DN_684) 2 = Direct capacity control - HTG/CLG mode (AI 1) 3 = Direct capacity control - DHW (AI 2) 4 = Direct capacity control - HTG/CLG (AI1) & DHW (AI2) | 680 | - | 0~4 | 0
| DHW setpoint temperature - analogue input (AI) selection: 0 = AI not used; 1 = AI 1; 2 = AI 2; 3 = AI 3 | 681 | - | 0~3 | 0
| Zone 1 setpoint temperature (HTG) - AI selection: 0 = AI not used; 1 = AI 1; 2 = AI 2; 3 = AI 3 | 682 | - | 0~3 | 0
| Zone 2 setpoint temperature (HTG) - AI selection: 0 = AI not used; 1 = AI 1; 2 = AI 2; 3 = AI 3 | 683 | - | 0~3 | 0
| Zone 1 setpoint temperature (CLG) - AI selection: 0 = AI not used; 1 = AI 1; 2 = AI 2; 3 = AI 3 | 684 | - | 0~3 | 0
| Upper limit of DHW setpoint temperature | 685 | - | 40~80 | 65
| Resolution of DHW setpoint temperature | 689 | - | 1~5 | 5
| Upper limit of Zone 1 setpoint temperature (HTG) | 686 | - | 20~55 (65) | 55
| Resolution of Zone 1 setpoint temperature (HTG) | 68A | - | 1~5 | 3
| Upper limit of Zone 2 setpoint temperature (HTG) | 687 | - | 20~55 (65) | 55
| Resolution of Zone 2 setpoint temperature (HTG) | 68B | - | 1~5 | 3
| Upper limit of Zone 1 setpoint temperature (CLG) | 688 | - | 7~29 | 20
| Resolution of Zone 1 setpoint temperature (CLG) | 68C |  | 1~5 | 1
| DN Description | Hydro | RC | Range HWT-60 (HWT-110) | Default HWT-60 (HWT-110) | After Commissioning | Change 1 | Change 2
System Set-Up (DPSW replacement) | Used to activate external boiler output: 0 = external boiler output de-activated 1 = external boiler output activated | 6B0 | - | 0~1 | 0
| Boiler install location: 0 = Heating side after 3 way diverting valve 1 = Before 3 way diverting valve | 6B1 | - | 0~1 | 0
| External cylinder thermostat connection: 0 = external cylinder thermostat not connected 1 = external cylinder thermostat connected | 6B2 | - | 0~1 | 0
| External room thermostat connection: 0 = external room thermostat not connected 1 = external room thermostat connected | 6B3 | - | 0~1 | 0
| Used to determine the 3 way diverting valve used on system: 2 = 2 wire spring return / 3 wire SPST type valve 1 = 3 wire SPDT type valve | 6B4 | - | 0~1 | 0
| Pump P2 synchronisation: 0 = P2 continuous operation (P2 OFF when RC OFF) 1 = Synchronised with pump P1 | 6B5 | - | 0~1 | 0
| DHW cylinder connection: 0 = DHW cylinder connected to system 1 = DHW cylinder not connected to system | 6B8 | - | 0~1 | 0
| Zone 1 operation - activation: 0 = Zone 1 operation activated 1 = Zone 1 operation de-activated | 6B9 | - | 0~1 | 0
| Zone 2 operation - activation: 0 = Zone 2 operation de-activated 1 = Zone 2 operation activated | 6BA | - | 0~1 | 0
| Pump P1 operation - heating mode: 0 = Normal / continuous operation 1 = STOP when OAT ≥ 20°C | 6D0 | - | 0~1 | 0
| Pump P1 ON/OFF cycling (during long periods of system OFF) 0 = Normal / continuous operation 1 = Intermittent operation Must be used with DN_BA (HTG.) and DN_BB (CLG.) | 6D1 | - | 0~1 | 0
| Hydro unit backup heater control activation 0 = back up heater control activated 1 = back up heater control de-activated | 6D2 | - | 0~1 | 0
| DHW cylinder heater control activation: 0 = DHW cylinder heater control activayed 1 = DHW cylinder heater control de-activated | 6D3 | - | 0~1 | 0
| External booster heater output activation: 0 = external booster heater output activated 1 = external booster heater output de-activated | 6D4 | - | 0~1 | 0
| Auto restart after power failure - activation 0 = auto restart de-activated 1 = auto restarts activated | 28 | - | 0~1 | 1
| Pump P1 operation for DHW: 0 = Synchronised with heat pump 1 = Continuous operation | 5A | - | 0~1 | 0
| Custom options for I/P7 / 8 (CN21): 0: I/P 7 = Forced stop input; I/P 8 = None 1: I/P 7 = TEMPO 1 input; I/P 8 = None 2: I/P 7 = TEMPO 2 input; I/P 8 = None 3: I/P 7 = Forcibly turn OFF bach up heater; I/P 8 = Forcibly turn OFF the hot water tank heater 4: I/P 7 = SMART Grid network input 1; I/P 8 = SMART Grid network input 2 | B6 | - | 0~4 | 0
Address setting | Line address | 12 | - | 1~128 | None
| Indoor address | 13 | - | 1~128 | None
| Group address 0 = Individual (Not group control) 1 = Header unit 2 = Follower unit | 14 | - | 0~2 | None
SG ready | The temperature increase during “Forced ON” mode (SG Ready control) | AC | - | 0~10 | 0
| SG ready forced operation heater control 0 = Heater output allowed 1 = Heater output not allowed | 6CE | - | 0~1 | 0
Power consumption | Power consumption function is using 0 = OFF 1 = ON | - | 1B | 0~1 | 1
Language setting | Language setting 0 = English 1 = Turkish … |  |  | 0~15 | 0

## R32 DN Codes_AIO
Location & DN Number
| DN Description | Hydro | RC | Range HWT-60 (HWT-110) | Default HWT-60 (HWT-110) | After Commissioning | Change 1 | Change 2
Setting Water Temperature Range | Heating Upper Limit - Zone 1 | 1A | - | 37~55°C (65°C) | 55 (65)
| Heating Lower Limit - Zone 1 | 1B | - | 20~37°C | 20
| Heating Upper Limit - Zone 2 | 1C | - | 37~55°C (65°C) | 55 (65)
| Heating Lower Limit - Zone 2 | 1D | - | 20~37°C | 20
| Cooling - Upper Limit | 18 | - | 18~30°C | 25
| Cooling - Lower Limit | 19 | - | 7~20°C | 7
| Hot Water - Upper limit | 1E | - | 60~65 | 65
| Hot Water - Lower limit | 1F | - | 40~60°C | 40
Hot Water Operation | Heat Pump Start Temperature | 20 | - | 20~45°C | 38
| Heat Pump Stop Temperature | 21 | - | 40~65°C | 52
| Group control - connection of TTW sensor: 0 = TTW sensor to be connected to each hydro unit 1 = TTW value transmitted from the HEADER unit | AB | - | 0~1 | 0
| Backup heater start time of heat-pump while hot water supply operating 0 = 30min passed 1 = 60min passed 2 = 90min passed 3 = 120min passed | 73 | - | 0~3 | 3
Hot Water Temperature Compensation | Temperature Compensation Outside Air Temperature (°C) | 24 | - | -20~10°C | 0
| Compensation Temperature (°C) | 25 | - | 0~15°C | 3
Hot Water Boost | Operation Time (x10 min) | 08 | - | 3~18 | 6
| Setting Temperature (°C) | 09 | - | 40~65 | 65
Anti Bacteria | Setting Temperature (°C) | 0A | - | 60~65 | 65
| Start Cycle (Day) | - | 0D | 1~10 | 7
| Start Time (Hour) | - | 0C | 0~23 | 22
| Operation Time (min) | 0B | - | 0~60 | 30
Priority Mode | Boiler & Heat Pump Switching Temperature (°C) | 23 | - | -20~20°C | -10
| Hot Water & Cooling priority selection: 0 = Cooling priority. Hot water produced by electric heater 1 = Hot water priority. Hot water produced by HP | 0F | - | 0~1 | 1
Heating Auto Curve Settings | Outside air temperature T0 (°C) | A1 | - | -20 (-30) ~ -15 (-20)°C | -20
| Outside air temperature T1 (°C) | 29 | - | -15~0°C | -10
| Outside air temperature T3 (°C) | 2B | - | 0~15°C | 10
| Setting Temperature A @ T0 (°C) - Zone 1 | 2C | - | 20~55°C (65°C) | 40
| Setting Temperature B @ T1 (°C) - Zone 1 | 2D | - | 20~55°C (65°C) | 35
| Setting Temperature C @ T2 (°C) - Zone 1 | 2E | - | 20~55°C (65°C) | 30
| Setting Temperature D @ T3 (°C) - Zone 1 | 2F | - | 20~55°C (65°C) | 25
| Setting Temperature E @ OAT 20°C (°C) - Zone 1 | 30 | - | 20~55°C (65°C) | 20
| Ratio Of Zone 2 In Zone 1 Auto Mode (%) | 31 | - | 0~100% | 80
| Zone 2 temperature setting 0=% (DN_31) ; 1 = Fixed (DN_A3~A5) | A2 | - | 0~1 | 0
| Setting temperature A' at T0 (°C) - Zone 2 | A3 | - | 20~55°C (65°C) | 40
| Setting temperature B' at T1 (°C) - Zone 2 | A4 | - | 20~55°C (65°C) | 35
| Setting temperature E' at 20°C (°C) - Zone 2 | A5 | - | 20~55°C (65°C) | 20
| Auto Curve - Temperature Shift (°C) | 27 | - | -5~5°C | 0
Frost Protection | Function 0=Invalid; 1=Valid | 3A | - | 0~1 | 1
| Frost Protection Setting Temperature (°C) | 3B | - | 8~20°C | 15
| Schedule end day | - | 12 | 0~20 | 0
| Schedule end time | - | 13 | 0~23 | 0
Back Up Heater Control | Downtime Back Up Heater 0=5min; 1=10min; 2=15min;3=20min | 33 | - | 0~3 | 1
| Uptime Back Up Heater 0=10min; 1=20min; 2=30min; 3=40min | 34 | - | 0~3 | 0
| Back up heater FORCE OFF at T0≥A°C: 0=no restriction; 1=20°C, 2=15°C….......6=-5°C | B8 | - | 0~6 | 0
| Back up heater operation during defrost control: β = TSC_F - THO 0 = 0K; 1 = 10K, 2 = 20K, 3 = 30K; 4 = 40K Recommendation: β = 2 = 20K | B9 | - | 0~4 | 0
| Backup heater capacity 0 = 3kW 1 = 6kW 2 = 9kW | 6BC | - | 0~2 | Depend on type
Night Setback | Change Setback Temperature (°C) | 26 | - | 3~20°C | 5
| Zone selection 0=Zone 1 & 2; 1= Zone 1 Only | 58 | - | 0~1 | 0
| Start Time (Hour) | - | 0E | 0~23 | 22
| End Time (Hour) | - | 0F | 0~23 | 6
Room Temperature Remote Controller | Temperature sensor using in room temperature control 0 = OFF 1 = ON | - | 1E | 0~1 | 0
| Room temperature control: 0 = Invalid; 1 = valid | 40 | - | 0~1 | 0
| Setting room temperature range: Cooling room temperature upper limit | 92 | - | 0 ~ 55 | 29
| Setting room temperature range: Cooling room temperature lower limit | 93 | - | 0 ~ 55 | 18
| Setting room temperature range: Heating room temperature upper limit | 94 | - | 0 ~ 55 | 29
| Setting room temperature range: Heating room temperature lower limit | 95 | - | 0 ~ 55 | 18
| Initial target water temperature in cooling with either room temperature controller or external room thermostat | 96 | - | 5 ~ 30 | 20
| Initial target water temperature in heating with either room temperature controller or external room thermostat | 9D | - | 20~55 (65) | 40
| Sets HP start temperature (water) when control is in A zone (2nd RC option only) | B2 | - | 20 ~ 37 | 25
| Initial water temperature setting method when controlling heating by the room temperature remote controller and room temperature thermostat: 0=Fixed temperature (DN_9D); 1=Calculated by Auto Curve (first time power up ONLY) | B5 | - | 0~1 | 0
| Room temperature offset: Heating room temperature offset value (sensor temp - control temp, K) | - | 02 | -10~10 | -1
| Room temperature offset: Cooling room temperature offset value (sensor temp - control temp, K) | - | 03 | -10~10 | -1
Hydro 2 Way Valve Operation Control | Cooling 2 Way Valve - Operation Logic: 0=Activated during cooling; 1=Not activated during cooling | 3C | - | 0~1 | 0
| DN Description | Hydro | RC | Range HWT-60 (HWT-110) | Default HWT-60 (HWT-110) | After Commissioning | Change 1 | Change 2
Hydro 3 Way Diverting Valve Operation Control | 3 Way Diverting Valve Operation Logic: 0=Activated during hot water operation; 1=not activated during hot water operation | 54 | - | 0~1 | 0
2 Zone Mixing Valve Drive Time | Specified Drive Time for Mixing Valve (x10sec) | 0C | - | 3~24 | 6
| Mixing valve OFF (control time - mins) 0=30sec; 1~30min | 59 | - | 0 = 30 sec, 1~30min | 2
| Temperature difference for mixing valve opening value changing | 6F1 | - | 1~3 | 2
| Mixing valve maximum steps | 6F2 | - | 12~60 | 60
Boiler/Heat Pump Synchronisation | External Boiler/Heat Pump Synchronisation 0=Synchronised, external boiler stops as temperature reaches the hydro unit's temperature setting ; 1=Not synchronised | 3E | - | 0~1 | 0
| System Operation during low ambient conditions: 0 = HP + boiler operation 1 = Boiler only operation (Pump P1 RUN) 2 = Electric heater only operation 3 = Boiler only (Pump P1 STOP) | 5B | - | 0~3 | 3
| Enable / Disable error code A02 (high return water control): 0 = A02 enabled 1 = A02 disabled | 62 | - | 0~1 | 0
| Used to activate external boiler output: 0 = external boiler output de-activated 1 = external boiler output activated | 6B0 | - | 0~1 | 0
| Boiler install location: 0 = Heating side after 3 way diverting valve 1 = Before 3 way diverting valve | 6B1 | - | 0~1 | 02
Maximum Operation Time Of Hot Water Heat Pump | Maximum Heat Pump Operation Time In Hot Water Operation Priority Mode (minutes) | 07 | - | 1~120 | 30
Cooling Operation | Select cooling mode: 0=Cooling & Heating Operation; 1=Heating Only Operation | 02 | - | 0~1 | 0
Remote Controller Indication | 24h or 12h Time Indication 0= 24h; 1=12h | - | 05 | 0~1 | 0
CDU Night Time Low Noise Operation | Low Noise Operation 0=Invalid; 1=Valid | - | 09 | 0~1 | 0
| Start Time (Hour) | - | 0A | 0~23 | 22
| End Time (Hour) | - | 0B | 0~23 | 6
Alarm Tone | Tone Switching 0=OFF; 1=ON | - | 11 | 0~1 | 1
Pump Control | Pump P1 operation during DHW mode: 0 = synchronised with heat pump 1 = Normal / continuous operation | 5A | - | 0~1 | 0
| Pump P2 operation in cooling mode: 0 = P2 continuous operation 1 = P2 stops in cooling operation | 64 | - | 0~1 | 0
| Synchronises pump P1 with room temperature control: 0 = P1 runs continuously 1 = P1 synchronised with room temperature control. When using the room temperature controller or the external room thermostat P1 will stop when HP in thermo OFF mode | 65 | - | 0~1 | 0
| Pump P1 operation: OAT temperature control in heating mode: P1 stops when TO > set value in DN_9E and DN_6D0=1 (heating mode only) | 9E | - | 10~30 | 20
| TO diff temperature, when pump P1 stop at TO 20°C | 6E | - | 1~5 | 2
| A-rated pump (P1) speed control. Changes the percentage duty of the PWM control. 00 = 100% PWM duty (Max. RPM) 01 = 90% ; 02 = 80%; 03 = 70%; 04 = 60% 05 = 50% | A0 | - | 0~5 | 0
| Pump P1 speed control method: 0 = fixed speed control (using DN_A0) 1 = variable speed control | 6A6 | - | 0~1 | 1
| Pump P1 speed correction for variable speed pump control: 0=100% Flmax; 1=90% Flmax; 2=75% Flmax; 3=50% FLmax | 6A7 | - | 0~3 | 0
| Pump P2 speed control (fixed speed): 0=100%; 1=80%; 2=70% Flmax; 3=60% | 6A1 | - | 0~3 | 0
| Pump P2 synchronisation: 0 = P2 continuous operation (P2 OFF when RC OFF) 1 = Synchronised with pump P1 | 6B5 | - | 0~1 | 1
| Pump P1 operation with OAT control: 0 = Normal / continuous operation 1 = P1 stopped when TO > 20°C | 6D0 | - | 0~1 | 0
| Pump P1 ON/OFF cycling (during long periods of system OFF) 0 = Normal / continuous operation 1 = Intermittent operation Must be used with DN_BA (HTG.) and DN_BB (CLG.) | 6D1 | - | 0~1 | 0
| Pump P1 Intermittent operation when T0 ≥ A°C (HTG.) 0 = continuous operation; 1 = 20°C; 2 = 15°C; 3 = 10°C; 4 = 5°C; 5 = 0°C; 6 = -5°C | BA | - | 0~6 | 0
| Pump P1 Intermittent operation when T0 < B°C (CLG.) 0 = continuous operation; 1 = 35°C; 2 = 30°C; 3 = 25°C | BB | - | 0~3 | 0
| Pump P2 on wireless adaptor screen (not on RC display): 0=Not Shown; 1=Shown | 42 | - | 0~1 | 0
| Pump off time during thermostat off operation 0 = 5min 1 = 10min … 5 = 30min | BC | - | 0~5 | 1
| DN Description | Hydro | RC | Range HWT-60 (HWT-110) | Default HWT-60 (HWT-110) | After Commissioning | Change 1 | Change 2
Operation By External Digital Input (optional) | Input signal setting when using I/P7 / 8 (CN21) as an a forced system STOP (and DN_B6 = 0) 0 = Contacts low > high system stop. System restart with remote controller 1 = Contacts high > low system stop. System restart with remote controller | 52 | - | 0~1 | 0
| Input signal setting when using I/P5 / 6 (CN21): 0 = Contacts high > low system STOP. Contacts low > high system restart 1 = Contacts low > high system STOP. Contacts low > high (2nd time - pulse input) system restart | 61 | - | 0~1 | 0
| Custom options for I/P7 / 8 (CN21): 0: I/P 7 = Forced stop input; I/P 8 = None 1: I/P 7 = TEMPO 1 input; I/P 8 = None 2: I/P 7 = TEMPO 2 input; I/P 8 = None 3: I/P 7 = Forcibly turn OFF bach up heater; I/P 8 = Forcibly turn OFF the hot water tank heater 4: I/P 7 = SMART Grid network input 1; I/P 8 = SMART Grid network input 2 | B6 | - | 0~4 | 0
Hydro Unit Digital Outputs | Output 1 options: 0 = alarm output 1 = Compressor operation output 2 = Defrost operation output 3 = Boiler control output 4 = Safety or protection control running 5 = Back up heater ON 6 = DHW cylinder heater ON 7 = Heating mode ON 8 = Cooling mode ON 9 = DHW mode ON | 6CA | - | 0~9 | 0
| Output 2 options: 0 = alarm output 1 = Compressor operation output 2 = Defrost operation output 3 = Boiler control output 4 = Safety or protection control running 5 = Back up heater ON 6 = DHW cylinder heater ON 7 = Heating mode ON 8 = Cooling mode ON 9 = DHW mode ON | 6CC | - | 0~9 | 2
| Output 3 options: 0 = alarm output 1 = Compressor operation output 2 = Defrost operation output 3 = Boiler control output 4 = Safety or protection control running 5 = Back up heater ON 6 = DHW cylinder heater ON 7 = Heating mode ON 8 = Cooling mode ON 9 = DHW mode ON | 6CD | - | 0~9 | 3
| Output 4 options: 0 = alarm output 1 = Compressor operation output 2 = Defrost operation output 3 = Boiler control output 4 = Safety or protection control running 5 = Back up heater ON 6 = DHW cylinder heater ON 7 = Heating mode ON 8 = Cooling mode ON 9 = DHW mode ON | 6CB | - | 0~9 | 1
Hydro Unit Type Setting | Hydro unit type setting: 70 = wall mounted hydro unit 71 = All In One type hydro unit | 10 | - | 70 or 71 | Depends on Hydro Unit
Hydro Unit Capacity Setting | Water heat exchanger capacity: 0010 = 401 / 601 0015 = 801 / 1101 | 11 | - | 0010 or 0015 | Depends on Hydro Unit
Outdoor unit type setting | Outdoor unit type setting 0 = 401/601 1 = 801/1101 2, 3 = None | 6BD | - | 0~3 | Depend on type
Floor Drying | Floor drying setting 0 = OFF 1 = ON | - | 1D | 0~1 | 0
| Setting START and END temperature (°C) | - | 14 | 20~55 | 0
| Setting maximum temperature (°C) | - | 15 | 20~55 | 0
| Continuation days for every step up to maximum temperature (days) | - | 16 | 1~7 | 0
| Temperature difference for every step up to maximum temperature (K) | - | 17 | 1~10 | 0
| Continuation days for every step down to end temperature (days) | - | 18 | 1~7 | 0
| Temperature difference for every step down to end temperature (K) | - | 19 | 1~10 | 0
| Continuation days at maximum temperature (days) | - | 1A | 1~50 | 0
0-10V Interface (optional) | ESTIA control type: 0 = Normal control 1 = Setpoint temperature control (DN_681~DN_684) 2 = Direct capacity control - HTG/CLG mode (AI 1) 3 = Direct capacity control - DHW (AI 2) 4 = Direct capacity control - HTG/CLG (AI1) & DHW (AI2) | 680 | - | 0~4 | 0
| DHW setpoint temperature - analogue input (AI) selection: 0 = AI not used; 1 = AI 1; 2 = AI 2; 3 = AI 3 | 681 | - | 0~3 | 0
| Zone 1 setpoint temperature (HTG) - AI selection: 0 = AI not used; 1 = AI 1; 2 = AI 2; 3 = AI 3 | 682 | - | 0~3 | 0
| Zone 2 setpoint temperature (HTG) - AI selection: 0 = AI not used; 1 = AI 1; 2 = AI 2; 3 = AI 3 | 683 | - | 0~3 | 0
| Zone 1 setpoint temperature (CLG) - AI selection: 0 = AI not used; 1 = AI 1; 2 = AI 2; 3 = AI 3 | 684 | - | 0~3 | 0
| Upper limit of DHW setpoint temperature | 685 | - | 40~65 | 65
| Resolution of DHW setpoint temperature | 689 | - | 1~5 | 5
| Upper limit of Zone 1 setpoint temperature (HTG) | 686 | - | 20~55 (65) | 55
| Resolution of Zone 1 setpoint temperature (HTG) | 68A | - | 1~5 | 3
| Upper limit of Zone 2 setpoint temperature (HTG) | 687 | - | 20~55 (65) | 55
| Resolution of Zone 2 setpoint temperature (HTG) | 68B | - | 1~5 | 3
| Upper limit of Zone 1 setpoint temperature (CLG) | 688 | - | 7~29 | 20
| Resolution of Zone 1 setpoint temperature (CLG) | 68C |  | 1~5 | 1
| DN Description | Hydro | RC | Range HWT-60 (HWT-110) | Default HWT-60 (HWT-110) | After Commissioning | Change 1 | Change 2
System Set-Up (DPSW replacement) | Used to activate external boiler output: 0 = external boiler output de-activated 1 = external boiler output activated | 6B0 | - | 0~1 | 0
| External room thermostat connection: 0 = external room thermostat not connected 1 = external room thermostat connected | 6B3 | - | 0~1 | 0
| Pump P2 synchronisation: 0 = P2 continuous operation (P2 OFF when RC OFF) 1 = Synchronised with pump P1 | 6B5 | - | 0~1 | 1
| DHW cylinder connection: 0 = DHW cylinder connected to system 1 = DHW cylinder not connected to system | 6B8 | - | 0~1 | 0
| Zone 1 operation - activation: 0 = Zone 1 operation activated 1 = Zone 1 operation de-activated | 6B9 | - | 0~1 | 0
| Zone 2 operation - activation: 0 = Zone 2 operation de-activated 1 = Zone 2 operation activated | 6BA | - | 0~1 | Depend on type
| Pump P1 operation - heating mode: 0 = Normal / continuous operation 1 = STOP when OAT ≥ 20°C | 6D0 | - | 0~1 | 0
| Pump P1 ON/OFF cycling (during long periods of system OFF) 0 = Normal / continuous operation 1 = Intermittent operation Must be used with DN_BA (HTG.) and DN_BB (CLG.) | 6D1 | - | 0~1 | 0
| Hydro unit backup heater control activation 0 = back up heater control activated 1 = back up heater control de-activated | 6D2 | - | 0~1 | 0
| DHW cylinder heater control activation: 0 = DHW cylinder heater control activayed 1 = DHW cylinder heater control de-activated | 6D3 | - | 0~1 | 0
| External booster heater output activation: 0 = external booster heater output activated 1 = external booster heater output de-activated | 6D4 | - | 0~1 | 0
| Auto restart after power failure - activation 0 = auto restart de-activated 1 = auto restarts activated | 28 | - | 0~1 | 1
| Pump P1 operation for DHW: 0 = Synchronised with heat pump 1 = Continuous operation | 5A | - | 0~1 | 0
| Custom options for I/P7 / 8 (CN21): 0: I/P 7 = Forced stop input; I/P 8 = None 1: I/P 7 = TEMPO 1 input; I/P 8 = None 2: I/P 7 = TEMPO 2 input; I/P 8 = None 3: I/P 7 = Forcibly turn OFF bach up heater; I/P 8 = Forcibly turn OFF the hot water tank heater 4: I/P 7 = SMART Grid network input 1; I/P 8 = SMART Grid network input 2 | B6 | - | 0~4 | 0
Address setting | Line address | 12 | - | 1~128 | None
| Indoor address | 13 | - | 1~128 | None
| Group address 0 = Individual (Not group control) 1 = Header unit 2 = Follower unit | 14 | - |  | None
SG ready | The temperature increase during “Forced ON” mode (SG Ready control) | AC | - | 0~10 | 0
| SG ready forced operation heater control 0 = Heater output allowed 1 = Heater output not allowed | 6CE | - | 0~1 | 0
Power consumption | Power consumption function is using 0 = OFF 1 = ON | - | 1B | 0~1 | 1
Language setting | Language setting 0 = English 1 = Turkish … |  |  | 0~15 | 0

## DPSWvDN Code Comparison
OK
| ESTIA Series 5 |  |  | ESTIA R32 Series 1
| DPSW No. | Default Setting | Description | ESTIA R32 DN Code | Range | Default Setting
| 02_1 | OFF | Boiler install location OFF = Heating side after 3 way valve ON = Before 3 way valve | 6B1 | 0~1 | 0
| 02_2 | Not Used
| 02_3 | OFF | External cylinder thermostat connection: OFF = cylinder thermostat not connected ON = cylinder thermostat connected | 6B2 | 0~1 | 0
| 02_4 | OFF | External room thermostat connection: OFF = room thermostat not connected ON = room thermostat connected | 6B3 | 0~1 | 0
| 10_1 | OFF | Pump P1 operation for DHW: OFF = Synchronised with heat pump ON = Continuous operation | 5A | 0~1 | 0
| 10_2 | OFF | Pump P1 operation for heating mode: OFF = Normal / continuous operation ON = Pump STOP when OAT ≥ 20°C | 6D0 | 0~1 | 0
| 10_3 | OFF | Pump P2 synchronisation; OFF = Pump P2 synchronised with pump P1 ON = Pump P2 continuous operation (pump OFF when RC OFF) | 6B5 | 0~1 | 0
| 10_4 | OFF | Pump P1 ON/OFF cycling - for long periods of system OFF: OFF = Normal operation ON = ON / OFF cycling available | 6D1 | 0~1 | 0
| 11_1 | OFF | Hydro unit backup heater control activation OFF = back up heater control activated ON = back up heater control de-activated | 6D2 | 0~1 | 0
| 11_2 | OFF | DHW cylinder heater control activation: OFF = DHW cylinder heater control activayed ON = DHW cylinder heater control de-activated | 6D3 | 0~1 | 0
| 11_3 | OFF | External booster heater output activation: OFF = external booster heater output activated ON = external booster heater output de-activated | 6D4 | 0~1 | 0
| 11_4 | Not Used
| 12_1 | OFF | DHW cylinder connection: OFF = DHW cylinder connected to system ON = DHW cylinder not connected to system | 6B8 | 0~1 | 0
| 12_2 | OFF | Zone 1 operation - activation: OFF = Zone 1 operation activated ON = Zone 1 operation de-activated | 6B9 | 0~1 | 0
| 12_3 | OFF | Zone 2 operation - activation OFF = Zone 2 operation de-activated ON = Zone 2 operation activated | 6BA | 0~1 | 0
| 12_4 | Not Used
| 13_1 | OFF | Type of 3 way diverting valve connected to system: OFF = 2 wire spring return or 3 wire SPST valve ON = 3 wire SPDT valve | 6B4 | 0~1 | 0
| 13_2 | OFF | External boiler output - activation OFF = external boiler output de-activated ON = external boiler output activated | 6B0 | 0~1 | 0
| 13_3 | OFF | Auto restart after power failure - activation OFF = auto restarts activated ON = auto restart de-activated | 28 | 0~1 | 0
| 13_4 | Not Used